## SCHEMATIC-TOP-EN
by JRV. 01/2022
De-Icing strategy InspirAIR® Top
| Marche Normale | <<<< NON<<<<< | Température extérieure à <-3°C pendant 30 minutes
˅˅˅˅˅˅ OUI˅˅˅˅˅
Normal operation | Fresh air T° < -3°C And Exhaust T° < 14°C During 15 minutes |  | With an installed and functional pre-heater | Fresh air T° < -3,5°C Exhaust T° < 4°C During 30 minutes | Normal operation
| Stage 1 : De-icing prevention |  | Stage 1 : Freezing mode | In "PassivHaus certification" configuration set via InspirAIR Controller or Aldes Configurator | Stage 1: Freezing mode
| Pre-heating coil is activating with a chrono-proportional setting : Each minute, the unit calculate how long the coil must be on go above the inital temp. |  | Both motors will stop |  | Only the insufflated air motor to the dweling will stop. Unit will continue to extract air at L1 speed
|  |  | up to 120 minutes motor stop* *If exhaust air is >14°C, the stopping time will be reduced |  | up to 120 minutes motor stop* *If exhaust air is >14°C, the stopping time will be reduced
up to 10 minutes of full battery operation in a row
Normal operation | Fresh air T° still < -3°C And Exhaust T° still < 4°C During 15 minutes
Stage 2 : Safe mode
Unit speed will be reduce to L1 airflow and coil again in Preating mode
up to 10 minutes of full battery operation in a row
Fresh air T° still < -3°C And Exhaust T° still < 4°C During 15 minutes
Stage 3: Freezing mode
Both motors will stop | In "PassivHaus certification" configuration set via InspirAIR Controller or Aldes Configurator |  | Only the insufflated air motor to the dweling will stop. Unit will continue to extract air at L1 speed
up to 120 minutes motor stop* *If exhaust air is >14°C, the stopping time will be reduced |  |  | up to 120 minutes motor stop* *If exhaust air is >14°C, the stopping time will be reduced
YES
YES
NO
YES
YES
NO
NO
YES
NO
YES
NO
YES
NO